## Watershed Treatment Plant
Caption: Boise Water Renewal ADA assessment findings, recommendations for remediation, and associated costs.
ID | LOCATION | BUILT BEFORE ADA | VIOLATIONS | 2010 ADA CODE | RECOMMENDATIONS | ESTIMATED COST | QUICK FIX | PRIORITY SCORE
1755 | Education Building Entrance | No | The interactive table is 41" above the floor. | §902.3 | The height of the interactive table is not directly specified in the ADA, but it would be more accessible to users in wheelchairs if its top were a max of 34" above the floor. | 1000 | No | 0
1721 | Wetlands Simulation | No | The benches do not have clear floor space for a wheelchair user to access the bench.The benches do not have back support. | §903.4, §903.2 | For the purposes of achieving greater accessibility and Human Centric Design, consider installing back support to some of the benches and pave a 30"x48" clear floor space at the end of some of the benches. | 5000 | No | 0
1734 | Education Building Outdoor Seating Area | No | The provided picnic table does not have an accessible clear space for a wheelchair user. | §226.1, §902, §305, §306 | Ensure that the wheelchair accessible seating has a clear floor space of 30" x 48" with a slope not steeper than 2% and that the tables have sufficient knee and toe clearance.Add/replace picnic tables so that at least 5% of the seating is wheelchair accessible. | 3000 | No | 3
1725 | Education Building Parking | No | The accessible car parking space has a 2.8% slope at the top. The accessible van parking space has a 3% slope at the bottom. The access aisle has a 2.7% slope down towards the accessible van parking space. | §502.4 | Reconstruct the parking spaces and access aisle to reduce the slope to a maximum of 2% in all directions. | 5000 | No | 3
1743 | Entire Facility | No | There is no tactile signage identifying 29 permanent room. | §216.2, §703 | Signs shall be Braille with raised lettering and should be placed on the wall in the center of an 18"x18" clear floor space.Install tactile signage on the latch side of the doorway at a height of 48” minimum to 60” maximum above the floor, identifying room by name or room number. | 2900 | No | 3
1838 | Head Works Building | No | The parking space has a 4% slope. | §502.4 | Reconstruct the parking space to reduce the slope to a maximum of 2% in all directions. | 2500 | No | 3
1728 | Laboratory Parking | No | There is no access aisle. | §502.3 | Install an access aisle connecting the accessible parking spaces to an accessible route. Each access aisle shall be 60” wide. | 1000 | No | 3
1715 | Nature Garden | No | The tables are located in the grass, therefore not accessible.The provided picnic table does not have an accessible clear space for a wheelchair user. | §226.1, §902, §305, §306 | Ensure that the wheelchair accessible seating has a clear floor space of 30" x 48" with a slope not steeper than 2% and that the tables have sufficient knee and toe clearance.Construct a firm, stable, and slip resistant accessible route with a maximum cross slope of 2% and maximum running slope of 5%. Add/replace picnic tables so that at least 5% of the seating is wheelchair accessible. | 5000 | No | 3
1716 | Nature Garden | No | There is not a firm, stable, and slip resistant route to the bench or garbage can. | §302.1, §305 | Or relocate the bench and garbage can adjacent to a level stable, firm, and slip resistant accessible route.Construct a firm, stable, and slip resistant accessible route with a maximum cross slope of 2% and maximum running slope of 5%. | 5000 | No | 3
1714 | Nature Garden | No | None of the play pockets are accessible. | §302.1, §305, ASTM F1951-99 | Replace the mulch with an accessible playground surface material such as pour-in-place rubber, rubber tiles, artificial grass, or engineered wood fiber. | 10000 | No | 3
1718 | Nature Garden | No | The path is not stable, firm, and slip resistant rendering the amenities inaccessible to persons with disabilities. | §302.1 | Ensure all amenities are located either on or directly adjacent to the new accessible surface.Replace the gravel with an accessible playground surface material such as pour-in-place rubber, rubber tiles, artificial grass, or engineered wood fiber. | 20000 | No | 3
1790 | New Head Works Path | No | The newly built path has a running slope of 8.9%. | §403.3 | Install handrails at a minimum height of 34" and maximum of 38" above the ground. Make sure there are adequate handrail extensions both at the top and bottom of the handrail.Reconstruct the route to reduce the running slope to a maximum of 5% or resurface the route to maximum slope to 8.3% making it a ramp. | 5000 | No | 3
1828 | Operations Building Entrance | No | The entrance has a 3.6% slope. | §404.2.4.4 | Reconstruct the entryway to reduce the running slope to a maximum of 2% in all directions for a distance of 60" perpendicular to the entryway. | 2500 | No | 3
1830 | Operations Building Parking | No | There is no level landing provided at the top of the curb ramp due to an 8.1% slope at the turning space. | §406.4 | Install a level landing at the top of the curb ramp with a minimum clear length of 36". | 1000 | No | 3
1834 | Operations Building Parking | No | The parking space and access aisle have a 2.7% slope and 4.1% slope. | §502.4 | Reconstruct the parking space and access aisle to reduce the slope to a maximum of 2% in all directions. | 2500 | No | 3
1730 | Ramp by Water Feature | No | The turning space has a 5.3% slope. | §304.2 | Reconstruct the turning space to reduce the slope to the maximum allowable 2% in all directions. | 2500 | No | 3
1720 | The Boise River Pathway | No | The running slope is 5.5%. | §403.3 | Resurface the route to reduce the running slope to a maximum of 5%. | 5000 | No | 3
1744 | Administration Break Room | No | There is no knee clearance underneath the sink.The dining and work surface counter is 34.75" above the floor. | §902.3, §306.3.3 | A portion of the dining and work surface must be no higher than 34” above the floor.Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. | 1000 | No | 5
1736 | Administration Restroom | No | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the rear wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
1752 | Administration Restroom Closest to Exit | No | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the rear wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
1754 | Administration Restroom Closest to Exit | No | The centerline of the toilet is located 19" from the sidewall. | §604.2 | Reposition the centerline of the toilet to be within 16" minimum and 18" maximum from the sidewall. | 1000 | No | 5
1836 | Aeration Basins | No | There is a 0.75" and 1" change in level. | §303.2 | Resurface the pathway to reduce the change in level to less than 0.25" or 0.5" if beveled. | 1000 | No | 5
1763 | Education Building Classroom | No | The sink is 36" above the floor. There is no knee clearance underneath the sink. | §606.3, §306.3.3 | Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor.Lower the sink to the maximum height of 34" above the floor. | 1000 | No | 5
1775 | Education Building Men’s Restroom | No | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the rear wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
1776 | Education Building Men’s Restroom | No | The centerline of the toilet is located 19" from the sidewall. | §604.2 | Reposition the centerline of the toilet to be within 16" minimum and 18" maximum from the sidewall. | 1000 | No | 5
1767 | Education Building Women’s Restroom | No | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the rear wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
1769 | Education Building Women’s Restroom | No | The centerline of the toilet is located 18.5" from the sidewall. | §604.2 | Reposition the centerline of the toilet to be within 16" minimum and 18" maximum from the sidewall. | 1000 | No | 5
1840 | Head Works Building | No | There is a 0.75" change in level. | §303.2 | Resurface the pathway to reduce the change in level to less than 0.25" or 0.5" if beveled. | 1000 | No | 5
1841 | Head Works Building | No | There is a 0.75" change in level. | §303.2 | Resurface the pathway to reduce the change in level to less than 0.25" or 0.5" if beveled. | 1000 | No | 5
1793 | New Head Works Path | No | There is a 1.75" change in level. | §303.2 | Resurface the pathway to reduce the change in level to less than 0.25" or 0.5" if beveled. | 1000 | No | 5
1791 | New Head Works Path | No | The bottom of the newly built path has a 0.75" change in level. | §303.2 | Pave a level landing with a minimum length of 60" and as wide as the ramp with a maximum slope shall be 2% in all directions.Resurface the pathway to reduce the change in level to less than 0.25" or 0.5" if beveled. | 2000 | No | 5
1803 | Operations Building Men’s Restroom | No | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the rear wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
1807 | Operations Building Men’s Restroom | No | The low urinal is 18.25" above the floor. | §605.2 | Lower the urinal to a maximum height of 17" above the floor. | 1000 | No | 5
1806 | Operations Building Men’s Restroom | No | The toilet is located 19" from the sidewall.The toilet is 19.5" above the floor. | §604.4, §604.2 | Lower the toilet seat to comply with the maximum height of 19” above the floor measured to the top of the seat.Reposition the toilet to be within 16" minimum and 18" maximum from the sidewall. | 1000 | No | 5
1817 | Operations Building Women’s Restroom | No | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the rear wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
1819 | Operations Building Women’s Restroom | No | The centerline of the toilet is located 18.5" from the sidewall. | §604.2 | Reposition the centerline of the toilet to be within 16" minimum and 18" maximum from the sidewall. | 1000 | No | 5
1723 | Wetlands Simulation | No | There is a 1" change in level. | §303.2 | Resurface the pathway to reduce the change in level to less than 0.25" or 0.5" if beveled. | 1000 | No | 5
1837 | Aeration Basins | No | Although this ramp is designed for vehicles, tours are led here to go to the Aeration Basins. The running slope of the ramp is 9.2%. There are no handrails. | §505.2, §405.2 | Install handrails at a minimum height of 34” and maximum of 38” above the ground. Make sure there are adequate handrail extensions both at the top and bottom of the handrail.Reconstruct the ramp to reduce the running slope to a maximum of 8.3% or consider allowing the patron's vehicle or an accessible golf cart traverse the ramp when needed. | 10000 | No | 6
1784 | Education Building | No | The height of the tall drinking fountain is not compliant at 36.75" above the floor. | §602.7 | Raise the existing tall drinking fountain in order to comply with the 38" minimum to 43" maximum spout height above the floor. | 1000 | No | 6
1787 | Education Building Entrance | No | There is only one drinking fountain provided at 36" above the floor. | §211.2, §602.7 | Install an additional drinking fountain at a minimum spout height of 38" and maximum of 43" above the floor. | 1000 | No | 6
1735 | Education Building Outdoor Seating Area | No | There is only one drinking fountain provided at 36" above the floor. | §211.2, §602.7 | Install an additional drinking fountain at a minimum spout height of 38" and maximum of 43" above the floor. | 1000 | No | 6
1825 | Operations Building Entrance | No | There is only one drinking fountain provided at 33.5" above the floor. | §211.2, §602.7 | Install an additional drinking fountain at a minimum spout height of 38" and maximum of 43" above the floor. | 1000 | No | 6
1799 | Operations Building Men’s Restroom | No | There is not an accessible shower provided. | §213.3.6 | Install at least one accessible shower complying with §607 or §608. | 10000 | No | 6
1788 | Education Building Ramp | No | The temporary ramp has a running slope of 27.5%. | §405.2 | Construct a ramp with a maximum running slope of 8.3% and a maximum cross slope of 2%. | 2500 | No | 7
1747 | Administration Break Room | No | The vending machine controls are outside of the unobstructed forward reach range at 60.5" above the floor. | §308.2.1 | This may require replacing the vending machine.Lower the vending machine controls by 12.5" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 3000 | No | 8
1760 | Education Building | No | The 15 interactive touch screens do not have any sound or tactile components.Therefore, a visually impaired person would not be able to access the information provided by the kiosk. | §707 | Since a fully touch screen interface can never be made fully ADA compliant, either replace the unit with an accessible one or provide an alternative accessible version. | 10000 | No | 8
1727 | Laboratory Parking | No | There are no markings on the left side of the accessible parking space. | §502 | Stripe the left side of the accessible parking space. | 1000 | No | 9
1833 | Operations Building Parking | No | The bicycles present an obstruction when parked in the access aisle. | §502.3 | Ensure that the bicycles are properly parked in the bike rack near the entrance. | 0 | Yes | 0
1847 | Head Works Building | No | There is no tactile sign identifying two permanent room. Doors serving as exits are not marked by tactile signage. | §216.2, §216.4, §703 | Place a tactile exit sign, that complies with §703.1, §703.2 and §703.5, identifying the exit doors. Signs shall be Braille with raised lettering and should be placed on the wall in the center of an 18"x18" clear floor space.Install tactile signage on the latch side of the doorway at a height of 48” minimum to 60” maximum above the floor, identifying room by name or room number. | 300 | Yes | 3
1717 | Nature Garden | No | There is no tactile sign identifying the permanent room. | §216.2, §703 | Signs shall be Braille with raised lettering and should be placed on the wall in the center of an 18"x18" clear floor space.Install tactile signage on the latch side of the doorway at a height of 48” minimum to 60” maximum above the floor, identifying room by name or room number. | 100 | Yes | 3
1829 | Operations Building Entrance | No | There is a 1" gap that is 0.75" deep at the entrance. | §302.3 | Fill in the gap. | 500 | Yes | 3
1811 | Operations Building Men’s Restroom | No | There is no tactile sign identifying the permanent room. | §216.2, §703 | Signs shall be Braille with raised lettering and should be placed on the wall in the center of an 18"x18" clear floor space.Install tactile signage on the latch side of the doorway at a height of 48” minimum to 60” maximum above the floor, identifying room by name or room number. | 100 | Yes | 3
1748 | Administration Conference Room | No | The TV protrudes 5.5" into the circulation space at 74" above the floor. | §307.2 | Recess the TV so it protrudes a maximum of 4", raise it so the bottom edge is 80" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
1749 | Administration Restroom | No | The first aid box protrudes 6.75" into the circulation space at 40.5" above the floor. | §307.2 | Recess the first aid box so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
1738 | Administration Restroom | No | The side grab bar is located 11.5" from the rear wall. | §604.5.1 | Remount the side grab bar 12" maximum from the rear wall and extending 54" minimum from the rear wall. | 500 | Yes | 5
1753 | Administration Restroom Closest to Exit | No | The side grab bar is located 11.5" from the rear wall. | §604.5.1 | Remount the side grab bar 12" maximum from the rear wall and extending 54" minimum from the rear wall. | 500 | Yes | 5
1731 | Education Building | No | The card scanner protrudes 8.5" into the circulation space at 38" above the floor. | §307.2 | Recess the card scanner so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
1783 | Education Building | No | The AED is outside of the unobstructed forward reach range at 49" above the floor.The AED protrudes 6" into the circulation space at 49" above the floor. | §307.2, §308.2.1 | Recess the AED so it protrudes a maximum of 4" or place a cane detectable object beneath it.Lower the AED by 1" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 5
1786 | Education Building Entrance | No | The card swipe protrudes 8.5" into the circulation space at 38" above the floor. | §307.2 | Recess the card swipe so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
1758 | Education Building Library | No | The TVs protrude 9" into the circulation space at 32.5" above the floor. | §307.2 | Recess the TVs so they protrude a maximum of 4", lower them so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath them. | 200 | Yes | 5
1778 | Education Building Men’s Restroom | No | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
1780 | Education Building Men’s Restroom | No | The hand dryer protrudes 8.25" into the circulation space at 47" above the floor. | §307.2 | Recess the hand dryer so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
1733 | Education Building Outdoor Seating Area | No | The card scanner protrudes 9" into the circulation space at 38.75" above the floor. | §307.2 | Recess the card scanner so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
1770 | Education Building Women’s Restroom | No | The space between the grab bar and toilet seat cover dispenser is 7.25". | §609.3 | Relocate the toilet seat cover dispenser to a location that is at least a distance of 12" or greater above the grab bar. Ensure that the toilet seat cover dispenser is not greater than 48" above the floor. | 100 | Yes | 5
1774 | Education Building Women’s Restroom | No | The hand dryer protrudes 8.5" into the circulation space at 47" above the floor. | §307.2 | Recess the hand dryer so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
1848 | Head Works Building | No | The first aid box is outside of the unobstructed forward reach range at 48.5" above the floor.The first aid box protrudes 5.5" into the circulation space at 48.5" above the floor. | §307.2, §308.2.1 | Recess the first aid box so it protrudes a maximum of 4" or place a cane detectable object beneath it.Lower the first aid box by 0.5" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 5
1826 | Operations Building Entrance | No | The sunscreen dispenser protrudes 6.75" into the circulation space at 34.5" above the floor. | §307.2 | Recess the sunscreen dispenser so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
1827 | Operations Building Entrance | No | The first aid box protrudes 5.75" into the circulation space at 47" above the floor. | §307.2 | Recess the first aid box so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
1805 | Operations Building Men’s Restroom | No | The space between the grab bar and the toilet seat cover dispenser is 10". | §609.3 | Relocate the toilet seat cover dispenser to a location that is at least a distance of 12" or greater above the grab bar. Ensure that the toilet seat cover dispenser is not greater than 48" above the floor. | 100 | Yes | 5
1797 | Operations Building Men’s Restroom | No | The benches do not have back support. | §903.4 | Back support shall be 2.5” maximum from the rear edge of the seat measured horizontally.At least 5% of the seating must provide back support that is 42” long minimum and extends from a point 2” maximum above the seat surface to a point 18” minimum above the seat surface. | 400 | Yes | 5
1820 | Operations Building Women’s Restroom | No | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
1818 | Operations Building Women’s Restroom | No | The side grab bar is located 11.5" from the rear wall. | §604.5.1 | Remount the side grab bar 12" maximum from the rear wall and extending 54" minimum from the rear wall. | 500 | Yes | 5
1816 | Operations Building Women’s Restroom | No | The tactile sign identifying the room is not in the correct location. | §703.4 | Reinstall the sign on the latch side of the door at 48" minimum above the floor measured from the baseline of the lowest character and 60" maximum measured from the baseline of the highest character. | 100 | Yes | 6
1741 | Administration Restroom | No | The mirror is too high to be accessible at 51" above the floor. | §603.3 | Lower the mirror so its bottom edge is a maximum height of 40" above the floor. | 100 | Yes | 7
1781 | Education Building Men’s Restroom | No | The mirror is too high to be accessible at 46.5" above the floor. | §603.3 | Lower the mirror so its bottom edge is a maximum height of 40" above the floor. | 100 | Yes | 7
1773 | Education Building Women’s Restroom | No | The mirror is too high to be accessible at 46.5" above the floor. | §603.3 | Lower the mirror so its bottom edge is a maximum height of 40" above the floor. | 100 | Yes | 7
1821 | Operations Building Laundry | No | The door knob requires twisting of the wrist. | §309.4 | Replace the door knob with a lever handle that can be operated with a closed fist and without twisting the wrist. | 100 | Yes | 7
1824 | Operations Building Laundry | No | The pipes under the sink are not covered. | §606.5 | Wrap the pipes beneath the sink with soft protective wrap or plastic. | 100 | Yes | 7
1809 | Operations Building Men’s Restroom | No | The mirror is too high to be accessible at 52" above the floor. | §603.3 | Lower the mirror so its bottom edge is a maximum height of 40" above the floor. | 100 | Yes | 7
1810 | Operations Building Men’s Restroom | No | The door knob requires twisting of the wrist. | §309.4 | Replace the door knob with a lever handle that can be operated with a closed fist and without twisting the wrist. | 100 | Yes | 7
1808 | Operations Building Men’s Restroom | No | The pipes under the sink are not covered. | §606.5 | Wrap the pipes beneath the sink with soft protective wrap or plastic. | 300 | Yes | 7
1813 | Operations Building Women’s Restroom | No | The mirror is too high to be accessible at 49" above the floor. | §603.3 | Lower the mirror so its bottom edge is a maximum height of 40" above the floor. | 100 | Yes | 7
1815 | Operations Building Women’s Restroom | No | The door knob requires twisting of the wrist. | §309.4 | Replace the door knob with a lever handle that can be operated with a closed fist and without twisting the wrist. | 100 | Yes | 7
1812 | Operations Building Women’s Restroom | No | The pipes under the sinks are not covered. | §606.5 | Wrap the pipes beneath the sinks with soft protective wrap or plastic. | 200 | Yes | 7
1746 | Administration Break Room | No | The paper towel dispenser is outside of the obstructed forward reach range at 58" above the floor. | §308.2.2 | Lower the paper towel dispenser by 10" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1739 | Administration Restroom | No | The toilet seat covers are outside of the unobstructed forward reach range at 59" above the floor. | §308.2.1 | Lower the toilet seat covers by 11" to meet the accessible reach range of 48" maximum above the floor and ensure it is at least 12" above the rear grab bar. | 100 | Yes | 8
1742 | Administration Restroom | No | The paper towel dispenser is outside of the unobstructed forward reach range at 54" above the floor. | §308.2.1 | This will require moving the changing table or the paper towel dispenser to another location.Lower the paper towel dispenser by 6" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1751 | Administration Restroom Closest to Exit | No | The paper towel dispenser is outside of the unobstructed forward reach range at 54" above the floor. | §308.2.1 | This will require moving the changing table or the paper towel dispenser to another location.Lower the paper towel dispenser by 6" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1732 | Education Building | No | The hooks are outside of the unobstructed forward reach range at 54" above the floor. | §308.2.1 | Lower at least one of the hooks by 6" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1764 | Education Building Classroom | No | The hand sanitizer dispenser is outside of the unobstructed forward reach range at 54" above the floor. | §308.2.1 | Lower the hand sanitizer dispenser by 6" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1766 | Education Building Classroom | No | The paper towel dispenser is outside of the unobstructed forward reach range at 56" above the floor. | §308.2.1 | Lower the paper towel dispenser by 8" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1757 | Education Building Library | No | The objects are outside of the unobstructed side reach range at 50" above the floor. | §308.3.1 | Lower the suggestion box by 2" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1779 | Education Building Men’s Restroom | No | The toilet seat covers are outside of the unobstructed forward reach range at 52" above the floor. | §308.2.1 | Lower the toilet seat covers by 4" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1771 | Education Building Women’s Restroom | No | The toilet seat covers are outside of the unobstructed forward reach range at 51" above the floor. | §308.2.1 | Lower the toilet seat covers by 3" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1842 | Head Works Building | No | The exit button is outside of the unobstructed forward reach range at 49.5" above the floor. | §308.2.1 | Lower the exit button by 1.5" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1843 | Head Works Building | No | The light switch is outside of the unobstructed forward reach range at 51" above the floor. | §308.2.1 | Lower the light switch by 3" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1844 | Head Works Building | No | The fire alarm is outside of the unobstructed forward reach range at 55" above the floor. | §308.2.1 | Lower the fire alarm by 7" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1845 | Head Works Building | No | The light switch is outside of the unobstructed forward reach range at 50" above the floor. | §308.2.1 | Lower the light switch by 2" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1846 | Head Works Building | No | The fire alarm is outside of the unobstructed forward reach range at 54" above the floor. | §308.2.1 | Lower the fire alarm by 6" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1823 | Operations Building Laundry | No | The paper towel dispenser is outside of the unobstructed forward reach range at 52" above the floor. | §308.2.1 | Lower the paper towel dispenser by 4" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1798 | Operations Building Men’s Restroom | No | The hooks are outside of the unobstructed forward reach range at 72.5" above the floor. | §308.2.1 | Lower at least one of the hooks by 24.5" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1802 | Operations Building Men’s Restroom | No | The hooks are outside of the unobstructed forward reach range at 71" above the floor. | §308.2.1 | Lower at least one of the hooks by 23" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1814 | Operations Building Women’s Restroom | No | The paper towel dispenser is outside of the unobstructed forward reach range at 50" above the floor. | §308.2.1 | Lower the paper towel dispenser by 2" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1726 | Education Building Parking | No | The parking signs identifying the accessible parking space do not meet the minimum height requirement of 60" from the ground. | §502.6 | Reinstall the accessible parking signs at each accessible space at a minimum height of 60" above the ground. | 200 | Yes | 9
1839 | Head Works Building | No | The accessible parking sign is 58.75" above the ground. | §502.6 | Remount the accessible parking sign at a minimum height of 60" above the ground. | 100 | Yes | 9
1729 | Laboratory Parking | No | The parking sign identifying the accessible parking space does not meet the minimum height requirement of 60" from the ground. | §502.6 | Install an accessible parking sign at each accessible space at a minimum height of 60" above the ground centered to the parking space. | 100 | Yes | 9
1835 | Operations Building Parking | No | There is no signage present identifying the accessible parking spaces. | §502.6 | Install an accessible parking sign at each accessible space at a minimum height of 60" above the ground. | 100 | Yes | 9
High (1-4) | 73900
Medium (5-7) | 52600
Low (8-10) | 16400
Total | 142900
Quick Fix | 8500