## City Hall West
Caption: City Hall West ADA assessment findings, recommendations for remediation, and associated costs.
ID | LOCATION | BUILT BEFORE ADA | VIOLATIONS | 2010 ADA CODE | RECOMMENDATIONS | ESTIMATED COST | QUICK FIX | PRIORITY SCORE
3245 | Gym | No | There is no tactile sign identifying the permanent room. | §216.2, §703 | Signs shall be Braille with raised lettering and should be placed on the wall in the center of an 18"x18" clear floor space.Install tactile signage on the latch side of the doorway at a height of 48” minimum to 60” maximum above the floor, identifying room by name or room number. | 100 | Yes | 3
3704 | Gym | No | There is no clear floor space to access the paper towel dispenser.The paper towel dispenser is outside of the unobstructed forward reach range at 50.5" above the floor. | §308.2.1, §305.5 | Lower the paper towel dispenser by 2.5" to meet the accessible reach range of 48" maximum above the floor.Relocate the paper towel dispenser to a location that allows for a 30"x48" clear floor space. | 100 | Yes | 3
3406 | AED | No | The AED protrudes 8.5" into the circulation space at 31" above the floor. | §307.2 | Recess the AED so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
3611 | Body Camera Room | No | The shelf protrudes 6" into the circulation space at 42.5" above the floor. | §307.2 | Recess the shelf so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
3072 | CID Women's Restroom | No | The dispenser protrudes 6.75" into the circulation space at 45" above the floor. | §307.2 | Recess the dispenser so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3443 | CID Women's Restroom | No | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
3449 | CID Women's Restroom | No | The toilet paper dispenser is located out of the accessible reach range. | §604.7 | The outlet of the dispenser shall be 15” minimum and 48” maximum above the floor and shall not be located behind.Remount the toilet paper dispenser to 7” minimum and 9” maximum in front of the water closet measured to the centerline of the dispenser. | 100 | Yes | 5
3496 | CID Women's Restroom | No | The paper towel dispenser protrudes 7" into the circulation space at 48" above the floor. | §307.2 | Recess the paper towel dispenser so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3174 | Fire Side Men's Restroom | No | The toilet paper dispenser is located out of the accessible reach range. | §604.7 | The outlet of the dispenser shall be 15” minimum and 48” maximum above the floor and shall not be located behind.Remount the toilet paper dispenser to 7” minimum and 9” maximum in front of the water closet measured to the centerline of the dispenser. | 100 | Yes | 5
3403 | Fire Side Men's Restroom | No | The paper towel dispenser is outside of the unobstructed forward reach range at 48.5" above the floor.The paper towels protrude 9" into the circulation space at 48.5" above the floor. | §307.2, §308.2.1 | Recess the paper towels so it protrudes a maximum of 4" or place a cane detectable object beneath it.Lower the paper towel dispenser by 0.5" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 5
3618 | Fire Side Men's Restroom | No | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
3201 | Fire Side Women's Restroom | No | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
3207 | Fire Side Women's Restroom | No | The toilet paper dispenser is located out of the accessible reach range. | §604.7 | The outlet of the dispenser shall be 15” minimum and 48” maximum above the floor and shall not be located behind.Remount the toilet paper dispenser to 7” minimum and 9” maximum in front of the water closet measured to the centerline of the dispenser. | 100 | Yes | 5
3635 | Fire Side Women's Restroom | No | The dispenser protrudes 5.75" into the circulation space at 39.75" above the floor. | §307.2 | Recess the dispenser so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3771 | Front Desk | No | The front desk protrudes 12.75" into the circulation space at 34" above the floor. | §307.2 | Extend the sides of the counter down to a maximum of 27" above the floor to provide cane detectability. | 100 | Yes | 5
3619 | Gun Shot Trauma Kit | No | The gun shot trauma kit protrudes 14" into the circulation space at 40.5" above the floor. | §307.2 | Recess the gun shot trauma kit so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
3488 | Holding Cell Restroom | No | The toilet paper dispenser is located out of the accessible reach range. | §604.7 | The outlet of the dispenser shall be 15” minimum and 48” maximum above the floor and shall not be located behind.Remount the toilet paper dispenser to 7” minimum and 9” maximum in front of the water closet measured to the centerline of the dispenser. | 100 | Yes | 5
3066 | Lobby | No | The lobby counter protrudes 12" into the circulation space at 33" above the floor. | §307.2 | Extend the sides of the counter down to a maximum of 27" above the floor to provide cane detectability. | 100 | Yes | 5
3265 | Lobby | No | The AED protrudes 6" into the circulation space at 32" above the floor. | §307.2 | Recess the AED so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
3270 | Lobby Gun Shot Trauma Kit | No | The gun shot trauma kit protrudes 15" into the circulation space at 40" above the floor. | §307.2 | Recess the gun shot trauma kit so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3056 | Lobby Women's Restroom | No | The sharps container protrudes 5" into the circulation space at 37.75" above the floor. | §307.2 | Recess the sharps container so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3275 | Lobby Women's Restroom | No | The toilet paper dispenser is located out of the accessible reach range. | §604.7 | The outlet of the dispenser shall be 15” minimum and 48” maximum above the floor and shall not be located behind.Remount the toilet paper dispenser to 7” minimum and 9” maximum in front of the water closet measured to the centerline of the dispenser. | 100 | Yes | 5
3727 | Locker Room AED | No | The AED protrudes 6.25" into the circulation space at 32" above the floor. | §307.2 | Recess the AED so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
3301 | Locker Room Shelves | No | The low shelf protrudes 9.75" into the circulation space at 67.5" above the floor. | §307.2 | Recess the low shelf so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3302 | Locker Room Shelves | No | The high shelf protrudes 9.75" into the circulation space at 75.75" above the floor. | §307.2 | Recess the high shelf so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3364 | Men's Restroom | No | The shelf protrudes 18" into the circulation space at 33" above the floor. | §307.2 | Extend the sides of the shelf down to a maximum of 27" above the floor to provide cane detectability. | 100 | Yes | 5
3414 | Men's Restroom | No | The paper towel dispenser protrudes 8" into the circulation space at 48.5" above the floor. | §307.2 | Recess the paper towel dispenser so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3681 | Men's Restroom | No | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
3577 | Men's Restroom by Lobby | No | The toilet paper dispenser is located out of the accessible reach range. | §604.7 | The outlet of the dispenser shall be 15” minimum and 48” maximum above the floor and shall not be located behind.Remount the toilet paper dispenser to 7” minimum and 9” maximum in front of the water closet measured to the centerline of the dispenser. | 100 | Yes | 5
3081 | Men's Restroom in CID | No | The dryer protrudes 9" into the circulation space at 48" above the floor. | §307.2 | Recess the dryer so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3356 | Men's Restroom in CID | No | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
3762 | Patrol Academy Classroom | No | The TV protrudes 7" into the circulation space at 57" above the floor. | §307.2 | Recess the TV so it protrudes a maximum of 4", raise it so the bottom edge is 80" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
3510 | Patrol Briefing | No | The TV protrudes 4.5" to 8" into the circulation space at 53" above the floor. | §307.2 | Recess the TV so it protrudes a maximum of 4", raise it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
3726 | Room 10 | No | The lock boxes protrude 6.5" into the circulation space at 47" above the floor. | §307.2 | Recess the lock boxes so they protrude a maximum of 4" or place a cane detectable object beneath them. | 100 | Yes | 5
3439 | Sawtooth Conference Room | No | The TV protrudes 7" into the circulation space at 72" above the floor. | §307.2 | Recess the TV so it protrudes a maximum of 4", raise it so the bottom edge is 80" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
3264 | Swat Memorabilia Shelf | No | The shelves protrude 15.25" into the circulation space at 30.5" above the floor. | §307.2 | Recess the shelves so they protrude a maximum of 4" or place a cane detectable object beneath them. | 100 | Yes | 5
3337 | Temporary Holding Cell | No | The table protrudes 24" into the circulation space at 29.5" above the floor. | §307.2 | Extend the sides of the table down to a maximum of 27" above the floor to provide cane detectability. | 100 | Yes | 5
3124 | Union Board | No | The shelf protrudes 9" into the circulation space at 29" above the floor. | §307.2 | Recess the shelf so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3061 | Women's Locker Room | No | The toilet paper dispenser is located out of the accessible reach range. | §604.7 | The outlet of the dispenser shall be 15” minimum and 48” maximum above the floor and shall not be located behind.Remount the toilet paper dispenser to 7” minimum and 9” maximum in front of the water closet measured to the centerline of the dispenser. | 100 | Yes | 5
3064 | Women's Locker Room | No | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
3120 | Women's Locker Room | No | The shelf protrudes 6.75" into the circulation space at 49.5" above the floor. | §307.2 | Recess the shelf so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
3362 | Exit | No | The tactile sign identifying the room is not in the correct location. | §703.4 | Reinstall the sign on the latch side of the door at 48" minimum above the floor measured from the baseline of the lowest character and 60" maximum measured from the baseline of the highest character. | 100 | Yes | 6
3289 | Exit by Kim | No | The tactile sign identifying the room is not in the correct location. | §703.4 | Reinstall the sign on the latch side of the door at 48" minimum above the floor measured from the baseline of the lowest character and 60" maximum measured from the baseline of the highest character. | 100 | Yes | 6
3022 | Exit by Lobby | No | The tactile sign identifying the room is not in the correct location. | §703.4 | Reinstall the sign on the latch side of the door at 48" minimum above the floor measured from the baseline of the lowest character and 60" maximum measured from the baseline of the highest character. | 100 | Yes | 6
3424 | Lobby Women's Restroom | No | The tactile sign identifying the room is not in the correct location. | §703.4 | Reinstall the sign on the latch side of the door at 48" minimum above the floor measured from the baseline of the lowest character and 60" maximum measured from the baseline of the highest character. | 100 | Yes | 6
3269 | Men's Locker Room | No | The tactile sign identifying the room is not in the correct location. | §703.4 | Reinstall the sign on the latch side of the door at 48" minimum above the floor measured from the baseline of the lowest character and 60" maximum measured from the baseline of the highest character. | 100 | Yes | 6
3643 | Men's Locker Room | No | The shower head is fixed. | §607.6 | Install a secondary handheld shower that is mounted a maximum of 48" above the floor. | 100 | Yes | 6
3318 | Personnel Entrance Lobby | No | The tactile sign identifying the room is not in the correct location. | §703.4 | Reinstall the sign on the latch side of the door at 48" minimum above the floor measured from the baseline of the lowest character and 60" maximum measured from the baseline of the highest character. | 100 | Yes | 6
3040 | Women's Locker Room | No | The shower spray unit hose is less than 59" long. | §607.6 | Install a new shower head with a 59" long minimum hose to allow for a user to sit or stand. | 100 | Yes | 6
3569 | Back Lot | No | There is not a firm, stable, and slip resistant route to the garbage can. | §302.1, §305 | Relocate the garbage can adjacent to the accessible route. | 100 | Yes | 7
3444 | CID Women's Restroom | No | The basket is outside of the unobstructed forward reach range at 51" above the floor. | §308.2.1 | Lower the basket by 3" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
3445 | CID Women's Restroom | No | The hook is outside of the unobstructed forward reach range at 65" above the floor. | §308.2.1 | Lower the hook by 17" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3542 | Facilities Office | No | The first aid box is outside of the unobstructed forward reach range at 51.75" above the floor. | §308.2.1 | Lower the first aid box by 3.75" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3528 | Fire Break Room | No | The paper towel dispenser is outside of the obstructed forward reach range at 54" above the floor. | §308.2.2 | Lower the paper towel dispenser by 6" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3003 | Fire Side Men's Restroom | No | The coat hook is outside of the unobstructed forward reach range at 64" above the floor. | §308.2.1 | Lower the coat hook by 16" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3202 | Fire Side Women's Restroom | No | The bin is outside of the unobstructed forward reach range at 51" above the floor. | §308.2.1 | Lower the bin by 3" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
3203 | Fire Side Women's Restroom | No | The hook is outside of the unobstructed forward reach range at 65" above the floor. | §308.2.1 | Lower the hook by 13" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3541 | Men's Restroom | No | The hook is outside of the unobstructed forward reach range at 60" above the floor. | §308.2.1 | Lower the hook by 12" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3574 | Men's Restroom by Lobby | No | The toilet seat covers are outside of the unobstructed forward reach range at 58" above the floor. | §308.2.1 | Lower the toilet seat covers by 10" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
3778 | Men's Restroom in CID | No | The hook is outside of the unobstructed forward reach range at 64" above the floor. | §308.2.1 | Lower the hook by 16" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3591 | Quarter Master Room | No | The paper towel dispenser is outside of the unobstructed forward reach range at 53" above the floor. | §308.2.1 | Lower the paper towel dispenser by 5" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3062 | Women's Locker Room | No | The basket is outside of the unobstructed forward reach range at 51" above the floor. | §308.2.1 | Lower the basket by 3" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
3063 | Women's Locker Room | No | The hook is outside of the unobstructed forward reach range at 63" above the floor. | §308.2.1 | Lower the hook by 15" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3157 | Women's Locker Room | No | The hook is outside of the unobstructed forward reach range at 70" above the floor. | §308.2.1 | Lower the hook by 22" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3215 | Women's Locker Room | No | The paper towel dispenser is outside of the unobstructed forward reach range at 53.5" above the floor. | §308.2.1 | Lower the paper towel dispenser by 5.5" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
3656 | Secure Back Lot Employee Parking | No | The accessible parking sign is 41.5" above the ground. | §502.6 | Remount the accessible parking sign at a minimum height of 60" above the ground. | 100 | Yes | 9
3567 | Patrol Academy Classroom | No | There are 1" wide and 5" deep gaps in the floor. | §302.3 | Replace the floor covers with one that have gaps that are a maximum of 0.5" wide. | 200 | Yes | 3
3605 | Fire Academy Classroom | No | The TVs protrude 5.5" into the circulation space at 57" above the floor. | §307.2 | Recess the TVs so they protrude a maximum of 4", raise them so the bottom edge is 80" maximum above the floor, or place a cane detectable object beneath them. | 200 | Yes | 5
3211 | Secure Back Lot Employee Parking | No | The parking signs identifying the accessible parking space do not meet the minimum height requirement of 60" from the ground. | §216.5 | Remount the accessible parking signs to ensure 60" minimum height from the ground. | 200 | Yes | 6
3165 | Fire Side Men's Restroom | No | The pipes under the sinks are not covered. | §606.5 | Wrap the pipes beneath the sinks with soft protective wrap or plastic. | 200 | Yes | 7
4487 | Men's Locker Room | No | The locks and hooks are outside of the unobstructed forward reach range at 57" and 73.5" above the floor. | §308.2.1 | At least 5%, but no fewer than one, locker shall be provided complying with §803.Lower the locks and hooks by 9" and 25.5" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 200 | Yes | 8
3659 | Coeur D'Alene | No | There are 1" wide and 5" deep gaps in the floor. | §302.3 | Replace the floor covers with ones that have gaps that are a maximum of 0.5" wide. | 300 | Yes | 3
3428 | Fire Academy Classroom | No | There are 1" wide and 5" deep gaps in the floor. | §302.3 | Replace the floor covers with ones that have a maximum width of 0.5". | 300 | Yes | 3
3055 | Sawtooth Auditorium | No | There are 1" wide and 5" deep gaps in the floor. | §302.3 | Replace the floor covers with one that have gaps that are a maximum of 0.5" wide. | 300 | Yes | 3
3617 | Lobby | No | The drinking fountain protrudes 17" into the circulation path. | §602, §307.2 | Place a drinking fountain skirt at this location to provide cane detectability. | 500 | Yes | 10
3358 | Men's Restroom by Lobby | No | The drinking fountain protrudes 18" into the circulation path. | §602, §307.2 | Place a drinking fountain skirt at this location to provide cane detectability. | 500 | Yes | 10
3210 | Secure Back Lot Employee Parking | No | There are tripping hazards in the accessible route. | §302.1 | Repave the area of the sidewalk to remove the crack. | 500 | Yes | 3
3401 | Parking | No | The parking signs identifying the accessible parking space do not meet the minimum height requirement of 60" from the ground | §216.5 | Remount the accessible parking signs to ensure 60" minimum height from the ground. | 500 | Yes | 6
3208 | Secure Back Lot Employee Parking | No | There are no marked "Van Accessible" spaces. | §208.2.4 | Install one 132" wide van accessible parking space. Add a “van accessible” parking sign at a minimum height of 60" above the ground. | 1000 | No | 2
3118 | Cafeteria Entrance | No | The entrance has a 3.5% slope. | §404.2.4.4 | Resurface the entryway to reduce the running slope to a maximum of 2% in all directions. | 1000 | No | 3
3363 | HR Curb Ramp | No | The cross slope is 3.5%. | §403.3 | Resurface the route to reduce the cross slope to a maximum of 2%. | 1000 | No | 3
3330 | Secure Back Lot Employee Parking | No | The cross slope is 3.5%. | §403.3 | Resurface the route to reduce the cross slope to a maximum of 2%. | 1000 | No | 3
3511 | Women's Locker Room | No | The turning space has a 3.6% slope. | §304.2 | Resurface the turning space to reduce the slope to the maximum allowable 2% in all directions. | 1000 | No | 3
3730 | Chief Assistant | No | The counter is 42" above the floor. | §904.4.1 | A portion of the service counter must be no higher than 36" above the floor for a horizontal distance of 36". | 1000 | No | 4
3614 | Fire Administration Front Counter | No | The counter is 49" above the ground. | §904.4.1 | A portion of the service counter must be no higher than 36" above the floor for a horizontal distance of 36". | 1000 | No | 4
3529 | Fire Break Room | No | There is no knee clearance underneath the counter. | §306.3.3 | Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. | 1000 | No | 5
3383 | Fire Side Men's Restroom | No | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the real wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
3604 | Fire Side Men's Restroom | No | The urinal is 18" above the floor. | §605.2 | Lower the urinal to a maximum height of 17" above the floor. | 1000 | No | 5
3204 | Fire Side Women's Restroom | No | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the rear wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
3580 | Men's Locker Room | No | The bench is not deep enough at 12" deep. | §903.3 | Provide back support that is 42” long minimum and extends from a point 2” maximum above the seat surface to a point 18” minimum above the seat surface.Install a supplementary accessible bench that is 42" long and 20" to 24" deep. | 1000 | No | 5
3789 | Men's Locker Room | No | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the real wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
3384 | Men's Restroom | No | The urinal is 17.5" above the floor. | §605.2 | Lower the urinal to a maximum height of 17" above the floor. | 1000 | No | 5
3499 | Men's Restroom in CID | No | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the real wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
3772 | Men's Restroom in CID | No | The urinal is 18" above the floor. | §605.2 | Lower the urinal to a maximum height of 17" above the floor. | 1000 | No | 5
3568 | Quarter Master Room | No | There is no knee clearance underneath the counter. | §306.3.3 | Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. | 1000 | No | 5
3761 | Women's Locker Room | No | The bench is not deep enough at 12" deep.The locks and hooks are outside of the unobstructed forward reach range at 57" and 73.5" above the floor. | §308.2.1, §903.3 | Lower the locks and hooks by 9" and 25.5" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. At least 5%, but no fewer than one, locker shall be provided complying with §803.Install a supplementary accessible bench that is 42" long and 20" to 24" deep. | 1000 | No | 5
3441 | HR Curb Ramp | No | The curb ramp has a 7% slope and there is only one handrail. | §505.2 | Install another handrail at a minimum height of 34” and maximum of 38” above the ground. Make sure there are adequate handrail extensions both at the top and bottom of the handrail. | 1000 | No | 6
3376 | Cafeteria | No | The dining and work surface counter is 37" above the floor. | §902.3 | A 30" portion of the dining and work surface must be no higher than 34” above the floor. | 1000 | No | 8
3183 | Fire Academy Classroom | No | The podium is 40" above the floor. | §902.3 | Lower the podium to a maximum of 34" above the floor or have a secondary 34" high surface available adjacent to the podium. | 1000 | No | 8
3151 | IT Help Desk | No | The dining and work surface counter is 36" above the floor. | §902.3 | A 30" portion of the dining and work surface must be no higher than 34” above the floor. | 1000 | No | 8
3590 | Patrol Briefing Room | No | The dining and work surface counter is 42" above the floor. | §902.3 | A 30" portion of the dining and work surface must be no higher than 34” above the floor. | 1000 | No | 8
3216 | Sawtooth Conference Room | No | The podium is 41" above the floor. | §902.3 | Lower the podium to a maximum of 34" above the floor or have a secondary 34" high surface available adjacent to the podium. | 1000 | No | 8
3734 | Sawtooth Auditorium | No | The sink is 36" above the floor. There is no knee clearance underneath the counter.The dining and work surface counter is 36" above the floor. | §902.3, §306.3.3, §606.3 | A 30" portion of the dining and work surface must be no higher than 34” above the floor.Lower the sink to the maximum height of 34" above the floor. Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. | 2000 | No | 5
3538 | HR Door | No | The entrance has a 4% slope. | §404.2.4.4 | Reconstruct the entryway to reduce the running slope to a maximum of 2% in all directions for a distance of 60". | 2500 | No | 3
3127 | Secure Back Lot Employee Parking | No | The entrance has a 3.5% slope. | §404.2.4.4 | Reconstruct the entryway to reduce the running slope to a maximum of 2% in all directions for a distance of 60". | 2500 | No | 3
3197 | Secure Back Lot Employee Parking | No | The running slope of the curb ramp is 10%. | §405.2 | Recosntruct the curb ramp to reduce the running slope to a maximum of 8.3%. | 2500 | No | 7
3139 | Parking | No | There is no level turning space at each of the three curb ramps. | §304.3.1 | Reconstruct the curb ramps to ensure that there is a level landing, a minimum of 60" deep, with slopes no greater than 2% in all directions. | 3000 | No | 3
3351 | Lobby | No | The vending machine controls are outside of the unobstructed forward reach range at 55" above the floor. | §308.2.1 | This may require replacing the vending machine.Lower the vending machine controls by 7" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 3000 | No | 8
3399 | Parking | No | The first accessible parking space is not of sufficient width at 93" wide. The parking space has a 3% running slope. | §208.2.4, §502.4, §502.2 | Resurface the parking space to reduce the slope to a maximum of 2% in all directions. Restripe the first accessible parking space to a minimum of 96" wide. | 5000 | No | 3
3198 | Secure Back Lot Employee Parking | No | The running slope of the curb ramp is 10%.There is not adequate turning space. | §304.3.1, §405.2 | Repave the curb ramp to ensure that there is a level turning space, a minimum of 60"x60"m at tge vase if the ramp in between the two sloped sides.Reconstruct the curb ramp to reduce the running slope to a maximum of 8.3%. | 5000 | No | 3
3317 | Men's Locker Room | No | The shower dimensions do not meet the requirements for a transfer type shower at 35" wide. | §608.2.1 | Expand the transfer type shower compartment to meet the minimum dimensions of 36"x36" measured at the center points of opposing sides with a 36" wide minimum entry on the face of the shower compartment. | 5000 | No | 6
3042 | Women's Locker Room | No | The shower dimensions do not meet the requirements for a transfer type shower at 36" deep and 35" wide. | §608.2.1 | Expand the transfer type shower compartment to meet the minimum dimensions of 36"x36" measured at the center points of opposing sides with a 36" wide minimum entry on the face of the shower compartment. | 5000 | No | 6
3497 | Entire Facility | No | There are no tactile signs identifying 176 permanent rooms. | §216.2, §703 | Signs shall be Braille with raised lettering and should be placed on the wall in the center of an 18"x18" clear floor space.Install tactile signage on the latch side of the doorway at a height of 48” minimum to 60” maximum above the floor, identifying room by name or room number. | 17600 | Yes | 3
High (1-4) | 44400
Medium (5-7) | 32400
Low (8-10) | 10800
Total | 87600
Quick Fix | 10500